## Slide 1: Applying led security lights in an electric cooperative

## Slide 2: Why should we look at leds?
Public image – look green
Put light where it is useful
  Dark Sky Compliance
  Minimize neighbor complaints
  Meet city lighting codes
Supposed longer life
Fewer maintenance trips
Lower operating cost
Better Light quality

## Slide 3: Public image
Legislatively driven media push for green initiatives
Availability of Led lighting reflects pro-active environmental attitude
Some companies are requiring led lighting
  Poor customer service
  Potential lost revenue
Gives marketing groups another feather in their hat

## Slide 4: Put light where it is useful
LED lighting is more directional
City lighting Ordinances
Dark sky compliance
  B.U.G. – Backlight, Uplight, Glare
  Model Lighting ordinance
  http://darksky.org/outdoorlighting/mlo
Minimize neighbor complaints

## Slide 5: Supposed longer life
Hps lights estimated to last 4-6 years with a 24,000 hour bulb life
Most manufacturers claim 20 year led lamp life (100,000+ hour bulb life)
No lightning protection in standard lights
10 kV mov arrestors for lightning protection in most led lamps
Warranty on standard lights varies from 1-5 years
5-10 year warranties on led lamps and drivers
Standard photocontrols have limited life – usually change with bulb
Led mfg’s recommend higher quality (more expensive) photocells for longer life

## Slide 6: Light Quality – Not just lumens

## Slide 7: LEDs – Increase visibility at night
Photo source: US DOE Gateway report,
San Francisco, CA (12/08)

## Slide 8: Fewer maintenance trips
Improve customer satisfaction
reduce maintenance workload
More productive use of maintenance personnel

## Slide 9: Lower operating cost
Energy consumption less than half typical hps for equivalent lighting
Fewer failures =
  fewer spare parts
  Reduced equipment inventory
  Lower O&M budget

## Slide 10: Do leds make ¢ent$ for your utility?
Required data for analysis
  Cost of light fixtures
  Cost of replacement bulbs
  Hourly cost of maintenance crew
  If available, the number of security lights serviced each year
  Utility’s $/kwh energy cost & $/kW demand charge
  $/month customer charge
  Estimated annual cost increase for purchased power in percent
  Estimated labor and material inflation rate

## Slide 11: Selecting a light
Determine what is important to you and your customer
  Uniformity of appearance
  Durability
  Remote disconnect
  Motion sensing
  Communication with scada
  Ability to dim lights during certain periods of time
  Number of potential failure modes
  Vendor reputation

## Slide 12: Selecting a light
Get them in your hands
If possible, do side by side comparisons
Perform field trials at employee homes
Perform field trials at customer sites
Get feedback

## Slide 13: Leds at Lake Region electric cooperative

## Slide 14: Our process
Started by contacting usual equipment vendors to see their offerings
Looked at trade-shows for equipment that local vendors did not carry
Created a feature/criteria list for the light we wanted
Ordered several sample lights
Performed a side-by-side comparison of the lights
developed a break-even analysis for the various lights
Selected the light we felt was the best fit for our coop

## Slide 15: Types of lights we looked at
Retrofit kits
Look-a-like lights (same look as traditional HPS)
Dark sky compliant lights (no refractor)
Lights with refractors
Lights with time-set dimmability
Lights with motion sensor
Lights with remote disconnect
Lights that were combinations of the above

## Slide 16: retrofit kits – Pros & Cons
Pros:
  Light output was very good
  Price point was good
  Light would literally look just like old lights
Cons:
  Labor intensive
  Can be done in the field, but wiring would be difficult
  Some kits fit differently depending on mfg of original head unit

## Slide 17: Look-a-like lights pros & cons
Pros:
  Light would literally look just like old lights
  Potential Customer backlash would be minimum
  More led’s in the head of light than retrofit kit
  Light quality was acceptable
Cons:
  Light was not as bright as hps light farther from the light
  Light was not as bright as retrofit kit
  Lights were not new-tech sexy

## Slide 18: Dark sky compliant light pros & cons
Pros:
  Lights do not project out or upward
  Minimize neighbor complaints
  Should meet any city lighting codes
Cons:
  Reach of light from fixture not as good
  Many models did not use refractors/diffusers – high glare

## Slide 19: Observations about Lights with refractors
Most had to be field installed – added time and cost
Some had the led’s built into the globe – concern about wind & hail damage
Some used same globe as old lights – flimsy & damage prone
One brand had a hardened polymer refractor – stronger, but still field installed
One brand used a shatter resistant glass dome refractor

## Slide 20: Observations about Lights with motion detection
Two brands offered this
Excited about concept
Both used same third party technology
Seemed more appropriate for parking lot lighting
Concern about third party technology in a new technology application
Lights that offered this seemed least durable

## Slide 21: Observations about Lights with remote disconnect
Uses a Bluetooth fob
Must be in close proximity to light
Can be disconnected from the ground
Can also be disconnected with a Bluetooth laptop (no issues with lights on same pole)
  Scada capable photocontrol (we did not evaluate)
  Operates using zigbee and other proprietary rf protocols
  can be remotely disconnected
  Requires a light fixture with dimmable driver

## Slide 22: Lrec selection criteria
Low glare
must have some form of refractor, but must be tightly mounted
Remote disconnect – we want to be able to disconnect the light without a bucket truck
Looks are not a major factor, but we are not opposed to a new form
Metal housing
10 year warranty
Unique serial number on lights so we can track actual life span

## Slide 23: Economics
Look at the sensitivity to changes in:
  Assumed life of hps fixtures
  Led fixture cost
  Inflation rate
  Wholesale power cost
  Hourly maintenance cost

## Slide 24: Sensitivity analysis – hps fixture life
Chart: Revenue Generated - HPS vs LED Yard Lights - 5 Year HPS Life
Mercury Vapor Existing | 46.635 | 92.9944 | 139.0767 | 184.8807 | 41.2466 | 86.4897 | 131.4501 | 176.1265 | 220.5176 | 45.3354 | 89.1513 | 132.6775 | 175.9125 | 218.8549 | 7.2902 | 49.643 | 91.6987 | 133.4559 | 174.913 | -78.6338
HPS Existing | 70.26 | 140.3625 | 210.3067 | 280.0918 | 161.6843 | 231.1489 | 300.452 | 369.5928 | 438.5706 | 289.4028 | 358.0519 | 426.5354 | 494.8526 | 563.0025 | 378.2841 | 446.097 | 513.7403 | 581.213 | 648.5142 | 422.6942
HPS Burnt Bulb | -96.8047 | -26.7022 | 43.242 | 113.0271 | 182.6524 | 58.4432 | 127.7463 | 196.8871 | 265.8649 | 334.6787 | 178.8068 | 247.2903 | 315.6075 | 383.7574 | 451.7393 | 259.2709 | 326.9142 | 394.3868 | 461.6881 | 528.817
HPS New | -158.8047 | -88.7022 | -18.758 | 51.0271 | 120.6524 | -3.5568 | 65.7463 | 134.8871 | 203.8649 | 272.6787 | 116.8068 | 185.2903 | 253.6075 | 321.7574 | 389.7393 | 197.2709 | 264.9142 | 332.3868 | 399.6881 | 466.817
LED | -295.9047 | -206.8077 | -117.774 | -28.804 | 60.1021 | 148.944 | 237.7212 | 326.4335 | 415.0806 | 503.6622 | 592.1778 | 680.6272 | 769.0101 | 857.326 | 945.5748 | 1033.756 | 1121.8693 | 1209.9144 | 1297.8909 | 1385.7984

## Slide 25: Sensitivity analysis – hps fixture life
Chart: Revenue Generated - HPS vs LED Yard Lights - 4 Year HPS Life
Mercury Vapor Existing | 46.635 | 92.9944 | 139.0767 | 1.2319 | 46.7561 | 91.9991 | 136.9596 | -25.0624 | 19.3286 | 63.4328 | 107.2487 | -81.866 | -38.6309 | 4.3114 | 46.9597 | -172.5269 | -130.4712 | -88.714 | -47.2568 | -300.8036
HPS Existing | 70.26 | 140.3625 | 210.3067 | 97.5357 | 167.161 | 236.6256 | 305.9287 | 169.601 | 238.5787 | 307.3925 | 376.0416 | 213.2685 | 281.5857 | 349.7356 | 417.7175 | 225.2491 | 292.8924 | 360.3651 | 427.6663 | 201.8463
HPS Burnt Bulb | -96.8047 | -26.7022 | 43.242 | 113.0271 | -5.3804 | 64.0842 | 133.3873 | 202.5281 | 59.8733 | 128.6871 | 197.3362 | 265.8197 | 95.9425 | 164.0925 | 232.0744 | 299.8874 | 99.4408 | 166.9135 | 234.2147 | 301.3437
HPS New | -158.8047 | -88.7022 | -18.758 | 51.0271 | -67.3804 | 2.0842 | 71.3873 | 140.5281 | -2.1267 | 66.6871 | 135.3362 | 203.8197 | 33.9425 | 102.0925 | 170.0744 | 237.8874 | 37.4408 | 104.9135 | 172.2147 | 239.3437
LED | -295.9047 | -206.8077 | -117.774 | -28.804 | 60.1021 | 148.944 | 237.7212 | 326.4335 | 415.0806 | 503.6622 | 592.1778 | 680.6272 | 769.0101 | 857.326 | 945.5748 | 1033.756 | 1121.8693 | 1209.9144 | 1297.8909 | 1385.7984

## Slide 26: Sensitivity analysis – hps fixture life
Chart: Revenue Generated - HPS vs LED Yard Lights - 3 Year HPS Life
Mercury Vapor Existing | 46.635 | 92.9944 | -39.2231 | 6.5809 | 52.1051 | -97.4849 | -52.5245 | -7.8481 | -176.3564 | -132.2522 | -88.4363 | -277.551 | -234.316 | -191.3736 | -402.9382 | -360.5855 | -318.5298 | -554.5579 | -513.1008 | -471.9451
HPS Existing | 70.26 | 140.3625 | 33.0678 | 102.8529 | 172.4782 | 48.269 | 117.5721 | 186.7129 | 44.0581 | 112.8719 | 181.521 | 18.7479 | 87.065 | 155.215 | -29.5035 | 38.3095 | 105.9527 | -102.7071 | -35.4059 | 31.7231
HPS Burnt Bulb | -96.8047 | -26.7022 | 43.242 | -69.529 | 0.096288 | 69.5609 | -60.62 | 8.5208 | 77.4985 | -71.6692 | -3.0201 | 65.4634 | -104.4137 | -36.2638 | 31.7181 | -160.7503 | -93.107 | -25.6344 | -242.7496 | -175.6207
HPS New | -158.8047 | -88.7022 | -18.758 | -131.529 | -61.9037 | 7.5609 | -122.62 | -53.4792 | 15.4985 | -133.6692 | -65.0201 | 3.4634 | -166.4137 | -98.2638 | -30.2819 | -222.7503 | -155.107 | -87.6344 | -304.7496 | -237.6207
LED | -295.9047 | -206.8077 | -117.774 | -28.804 | 60.1021 | 148.944 | 237.7212 | 326.4335 | 415.0806 | 503.6622 | 592.1778 | 680.6272 | 769.0101 | 857.326 | 945.5748 | 1033.756 | 1121.8693 | 1209.9144 | 1297.8909 | 1385.7984

## Slide 27: Sensitivity analysis – hps fixture life
Chart: 20 Year Present Worth Comparison - 5 Year HPS Life
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 683.8085 | 347.3557 | 1031.1642
 | 1 | 2 | 3

## Slide 28: Sensitivity analysis – hps fixture life
Chart: 20 Year Present Worth Comparison - 5 Year HPS Life
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 683.8085 | 347.3557 | 1031.1642
 | 1 | 2 | 3

## Slide 29: Sensitivity analysis – hps fixture life
Chart: 10 Year Present Worth Comparison - 3 Year HPS Life
| 10 Year Present Worth LED vs. HPS | 10 Year Present worth HPS | 10 Year Present Worth LED
 | 474.2344 | -99.4624 | 374.772
 | 1 | 2 | 3

## Slide 30: Sensitivity analysis – hps fixture life
Chart: 20 Year Present Worth Comparison - 3 Year HPS Life
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 1207.9763 | -176.8121 | 1031.1642
 | 1 | 2 | 3

## Slide 31: Sensitivity analysis – fixture cost
Chart: Revenue Generated - HPS vs LED Yard Lights - 5 Year HPS Life
Mercury Vapor Existing | 46.635 | 92.9944 | 139.0767 | 184.8807 | 41.2466 | 86.4897 | 131.4501 | 176.1265 | 220.5176 | 45.3354 | 89.1513 | 132.6775 | 175.9125 | 218.8549 | 7.2902 | 49.643 | 91.6987 | 133.4559 | 174.913 | -78.6338
HPS Existing | 70.26 | 140.3625 | 210.3067 | 280.0918 | 161.6843 | 231.1489 | 300.452 | 369.5928 | 438.5706 | 289.4028 | 358.0519 | 426.5354 | 494.8526 | 563.0025 | 378.2841 | 446.097 | 513.7403 | 581.213 | 648.5142 | 422.6942
HPS Burnt Bulb | -96.8047 | -26.7022 | 43.242 | 113.0271 | 182.6524 | 58.4432 | 127.7463 | 196.8871 | 265.8649 | 334.6787 | 178.8068 | 247.2903 | 315.6075 | 383.7574 | 451.7393 | 259.2709 | 326.9142 | 394.3868 | 461.6881 | 528.817
HPS New | -158.8047 | -88.7022 | -18.758 | 51.0271 | 120.6524 | -3.5568 | 65.7463 | 134.8871 | 203.8649 | 272.6787 | 116.8068 | 185.2903 | 253.6075 | 321.7574 | 389.7393 | 197.2709 | 264.9142 | 332.3868 | 399.6881 | 466.817
LED | -295.9047 | -206.8077 | -117.774 | -28.804 | 60.1021 | 148.944 | 237.7212 | 326.4335 | 415.0806 | 503.6622 | 592.1778 | 680.6272 | 769.0101 | 857.326 | 945.5748 | 1033.756 | 1121.8693 | 1209.9144 | 1297.8909 | 1385.7984

## Slide 32: Sensitivity analysis – fixture cost
Chart: Revenue Generated - HPS vs LED Yard Lights - 25% Reduction in LED Cost
Mercury Vapor Existing | 46.635 | 92.9944 | 139.0767 | 184.8807 | 41.2466 | 86.4897 | 131.4501 | 176.1265 | 220.5176 | 45.3354 | 89.1513 | 132.6775 | 175.9125 | 218.8549 | 7.2902 | 49.643 | 91.6987 | 133.4559 | 174.913 | -78.6338
HPS Existing | 70.26 | 140.3625 | 210.3067 | 280.0918 | 161.6843 | 231.1489 | 300.452 | 369.5928 | 438.5706 | 289.4028 | 358.0519 | 426.5354 | 494.8526 | 563.0025 | 378.2841 | 446.097 | 513.7403 | 581.213 | 648.5142 | 422.6942
HPS Burnt Bulb | -96.8047 | -26.7022 | 43.242 | 113.0271 | 182.6524 | 58.4432 | 127.7463 | 196.8871 | 265.8649 | 334.6787 | 178.8068 | 247.2903 | 315.6075 | 383.7574 | 451.7393 | 259.2709 | 326.9142 | 394.3868 | 461.6881 | 528.817
HPS New | -158.8047 | -88.7022 | -18.758 | 51.0271 | 120.6524 | -3.5568 | 65.7463 | 134.8871 | 203.8649 | 272.6787 | 116.8068 | 185.2903 | 253.6075 | 321.7574 | 389.7393 | 197.2709 | 264.9142 | 332.3868 | 399.6881 | 466.817
LED | -239.9047 | -150.8077 | -61.774 | 27.196 | 116.1021 | 204.944 | 293.7212 | 382.4335 | 471.0806 | 559.6622 | 648.1778 | 736.6272 | 825.0101 | 913.326 | 1001.5748 | 1089.756 | 1177.8693 | 1265.9144 | 1353.8909 | 1441.7984

## Slide 33: Sensitivity analysis – fixture cost
Chart: 20 Year Present Worth Comparison - 5 Year HPS Life
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 683.8085 | 347.3557 | 1031.1642
 | 1 | 2 | 3

## Slide 34: Sensitivity analysis – fixture cost
Chart: 20 Year Present Worth Comparison - 25% reduction in fixture cost
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 725.4777 | 347.3557 | 1072.8334
 | 1 | 2 | 3

## Slide 35: Sensitivity analysis – inflation rate
Chart: Revenue Generated - HPS vs LED Yard Lights – 3% Inflation Rate
Mercury Vapor Existing | 46.635 | 92.9944 | 139.0767 | 184.8807 | 41.2466 | 86.4897 | 131.4501 | 176.1265 | 220.5176 | 45.3354 | 89.1513 | 132.6775 | 175.9125 | 218.8549 | 7.2902 | 49.643 | 91.6987 | 133.4559 | 174.913 | -78.6338
HPS Existing | 70.26 | 140.3625 | 210.3067 | 280.0918 | 161.6843 | 231.1489 | 300.452 | 369.5928 | 438.5706 | 289.4028 | 358.0519 | 426.5354 | 494.8526 | 563.0025 | 378.2841 | 446.097 | 513.7403 | 581.213 | 648.5142 | 422.6942
HPS Burnt Bulb | -96.8047 | -26.7022 | 43.242 | 113.0271 | 182.6524 | 58.4432 | 127.7463 | 196.8871 | 265.8649 | 334.6787 | 178.8068 | 247.2903 | 315.6075 | 383.7574 | 451.7393 | 259.2709 | 326.9142 | 394.3868 | 461.6881 | 528.817
HPS New | -158.8047 | -88.7022 | -18.758 | 51.0271 | 120.6524 | -3.5568 | 65.7463 | 134.8871 | 203.8649 | 272.6787 | 116.8068 | 185.2903 | 253.6075 | 321.7574 | 389.7393 | 197.2709 | 264.9142 | 332.3868 | 399.6881 | 466.817
LED | -295.9047 | -206.8077 | -117.774 | -28.804 | 60.1021 | 148.944 | 237.7212 | 326.4335 | 415.0806 | 503.6622 | 592.1778 | 680.6272 | 769.0101 | 857.326 | 945.5748 | 1033.756 | 1121.8693 | 1209.9144 | 1297.8909 | 1385.7984

## Slide 36: Sensitivity analysis – Inflation Rate
Chart: Revenue Generated - HPS vs LED Yard Lights - 7% Inflation Rate
Mercury Vapor Existing | 46.635 | 92.9944 | 139.0767 | 184.8807 | 10.1064 | 55.3494 | 100.3099 | 144.9863 | 189.3773 | -75.4986 | -31.6827 | 11.8435 | 55.0785 | 98.0209 | -292.6914 | -250.3387 | -208.283 | -166.5258 | -125.0686 | -691.7236
HPS Existing | 70.26 | 140.3625 | 210.3067 | 280.0918 | 130.7294 | 200.1939 | 269.4971 | 338.6379 | 407.6156 | 169.2878 | 237.9369 | 306.4204 | 374.7375 | 442.8875 | 80.0873 | 147.9003 | 215.5436 | 283.0162 | 350.3175 | -186.7477
HPS Burnt Bulb | -96.8047 | -26.7022 | 43.242 | 113.0271 | 182.6524 | 17.8001 | 87.1032 | 156.244 | 225.2218 | 294.0356 | 34.0431 | 102.5266 | 170.8438 | 238.9937 | 306.9756 | -86.1482 | -18.5049 | 48.9677 | 116.269 | 183.3979
HPS New | -158.8047 | -88.7022 | -18.758 | 51.0271 | 120.6524 | -44.1999 | 25.1032 | 94.244 | 163.2218 | 232.0356 | -27.9569 | 40.5266 | 108.8438 | 176.9937 | 244.9756 | -148.1482 | -80.5049 | -13.0323 | 54.269 | 121.3979
LED | -295.9047 | -206.8077 | -117.774 | -28.804 | 60.1021 | 148.944 | 237.7212 | 326.4335 | 415.0806 | 503.6622 | 592.1778 | 680.6272 | 769.0101 | 857.326 | 945.5748 | 1033.756 | 1121.8693 | 1209.9144 | 1297.8909 | 1385.7984

## Slide 37: Sensitivity analysis – inflation rate
Chart: 20 Year Present Worth Comparison – 3% Inflation Rate
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 683.8085 | 347.3557 | 1031.1642
 | 1 | 2 | 3

## Slide 38: Sensitivity analysis – inflation rate
Chart: 20 Year Present Worth Comparison - 7% INflation Rate
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 642.7571 | 61.7125 | 704.4697
 | 1 | 2 | 3

## Slide 39: Sensitivity analysis – Wholesale Power Cost
Chart: Revenue Generated - HPS vs LED Yard Lights – 0.5% Annual Power Cost Increase
Mercury Vapor Existing | 46.635 | 92.9944 | 139.0767 | 184.8807 | 41.2466 | 86.4897 | 131.4501 | 176.1265 | 220.5176 | 45.3354 | 89.1513 | 132.6775 | 175.9125 | 218.8549 | 7.2902 | 49.643 | 91.6987 | 133.4559 | 174.913 | -78.6338
HPS Existing | 70.26 | 140.3625 | 210.3067 | 280.0918 | 161.6843 | 231.1489 | 300.452 | 369.5928 | 438.5706 | 289.4028 | 358.0519 | 426.5354 | 494.8526 | 563.0025 | 378.2841 | 446.097 | 513.7403 | 581.213 | 648.5142 | 422.6942
HPS Burnt Bulb | -96.8047 | -26.7022 | 43.242 | 113.0271 | 182.6524 | 58.4432 | 127.7463 | 196.8871 | 265.8649 | 334.6787 | 178.8068 | 247.2903 | 315.6075 | 383.7574 | 451.7393 | 259.2709 | 326.9142 | 394.3868 | 461.6881 | 528.817
HPS New | -158.8047 | -88.7022 | -18.758 | 51.0271 | 120.6524 | -3.5568 | 65.7463 | 134.8871 | 203.8649 | 272.6787 | 116.8068 | 185.2903 | 253.6075 | 321.7574 | 389.7393 | 197.2709 | 264.9142 | 332.3868 | 399.6881 | 466.817
LED | -295.9047 | -206.8077 | -117.774 | -28.804 | 60.1021 | 148.944 | 237.7212 | 326.4335 | 415.0806 | 503.6622 | 592.1778 | 680.6272 | 769.0101 | 857.326 | 945.5748 | 1033.756 | 1121.8693 | 1209.9144 | 1297.8909 | 1385.7984

## Slide 40: Sensitivity analysis – Wholesale Power Cost
Chart: Revenue Generated - HPS vs LED Yard Lights - 4% Annual Power Cost
Mercury Vapor Existing | 46.635 | 91.065 | 133.2018 | 172.9537 | 21.0669 | 55.7589 | 87.7682 | 116.9875 | 143.3051 | -52.6813 | -32.5197 | -15.6222 | -2.1191 | 7.8538 | -240.0578 | -237.5748 | -239.0629 | -244.681 | -254.5941 | -563.6766
HPS Existing | 70.26 | 139.26 | 206.9496 | 273.2764 | 150.153 | 213.5885 | 275.4909 | 335.7991 | 394.4492 | 233.3933 | 288.5256 | 341.7928 | 393.1203 | 442.4305 | 236.9423 | 281.9726 | 324.7337 | 365.1348 | 403.0816 | 145.5269
HPS Burnt Bulb | -96.8047 | -27.8047 | 39.8849 | 106.2117 | 171.1211 | 40.8828 | 102.7852 | 163.0934 | 221.7435 | 278.6691 | 109.2805 | 162.5477 | 213.8751 | 263.1853 | 310.3975 | 95.1464 | 137.9075 | 178.3087 | 216.2554 | 251.6497
HPS New | -158.8047 | -89.8047 | -22.1151 | 44.2117 | 109.1211 | -21.1172 | 40.7852 | 101.0934 | 159.7435 | 216.6691 | 47.2805 | 100.5477 | 151.8751 | 201.1853 | 248.3975 | 33.1464 | 75.9075 | 116.3087 | 154.2554 | 189.6497
LED | -295.9047 | -207.2487 | -119.1169 | -31.5302 | 55.4896 | 141.9198 | 227.7368 | 312.916 | 397.4321 | 481.2583 | 564.3673 | 646.7301 | 728.3171 | 809.0972 | 889.0381 | 968.1062 | 1046.2666 | 1123.4831 | 1199.7178 | 1274.9315

## Slide 41: Sensitivity analysis – Wholesale Power Cost
Chart: 20 Year Present Worth Comparison – 0.5% Annual Power Cost
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 683.8085 | 347.3557 | 1031.1642
 | 1 | 2 | 3

## Slide 42: Sensitivity analysis – Wholesale Power Cost
Chart: 20 Year Present Worth Comparison - 4% Annual Power Cost
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 807.5516 | 141.1172 | 948.6688
 | 1 | 2 | 3

## Slide 43: Sensitivity analysis – Hourly Maintenance Cost
Chart: Revenue Generated - HPS vs LED Yard Lights – $161 Hourly Rate
Mercury Vapor Existing | 46.635 | 92.9944 | 139.0767 | 184.8807 | 41.2466 | 86.4897 | 131.4501 | 176.1265 | 220.5176 | 45.3354 | 89.1513 | 132.6775 | 175.9125 | 218.8549 | 7.2902 | 49.643 | 91.6987 | 133.4559 | 174.913 | -78.6338
HPS Existing | 70.26 | 140.3625 | 210.3067 | 280.0918 | 161.6843 | 231.1489 | 300.452 | 369.5928 | 438.5706 | 289.4028 | 358.0519 | 426.5354 | 494.8526 | 563.0025 | 378.2841 | 446.097 | 513.7403 | 581.213 | 648.5142 | 422.6942
HPS Burnt Bulb | -96.8047 | -26.7022 | 43.242 | 113.0271 | 182.6524 | 58.4432 | 127.7463 | 196.8871 | 265.8649 | 334.6787 | 178.8068 | 247.2903 | 315.6075 | 383.7574 | 451.7393 | 259.2709 | 326.9142 | 394.3868 | 461.6881 | 528.817
HPS New | -158.8047 | -88.7022 | -18.758 | 51.0271 | 120.6524 | -3.5568 | 65.7463 | 134.8871 | 203.8649 | 272.6787 | 116.8068 | 185.2903 | 253.6075 | 321.7574 | 389.7393 | 197.2709 | 264.9142 | 332.3868 | 399.6881 | 466.817
LED | -295.9047 | -206.8077 | -117.774 | -28.804 | 60.1021 | 148.944 | 237.7212 | 326.4335 | 415.0806 | 503.6622 | 592.1778 | 680.6272 | 769.0101 | 857.326 | 945.5748 | 1033.756 | 1121.8693 | 1209.9144 | 1297.8909 | 1385.7984

## Slide 44: Sensitivity analysis – Hourly Maintenance Cost
Chart: Revenue Generated - HPS vs LED Yard Lights - $350 Hourly Rate
Mercury Vapor Existing | 46.635 | 92.9944 | 139.0767 | 184.8807 | -170.8507 | -125.6076 | -80.6472 | -35.9708 | 8.4203 | -412.6408 | -368.8249 | -325.2987 | -282.0637 | -239.1213 | -735.727 | -693.3743 | -651.3185 | -609.5614 | -568.1042 | -1152.0917
HPS Existing | 70.26 | 140.3625 | 210.3067 | 280.0918 | -50.413 | 19.0516 | 88.3547 | 157.4955 | 226.4733 | -168.5734 | -99.9243 | -31.4408 | 36.8764 | 105.0263 | -364.7332 | -296.9202 | -229.2769 | -161.8043 | -94.503 | -650.7637
HPS Burnt Bulb | -285.2504 | -215.1479 | -145.2037 | -75.4186 | -5.7933 | -348.4627 | -279.1596 | -210.0188 | -141.0411 | -72.2272 | -481.3544 | -412.8709 | -344.5537 | -276.4038 | -208.4219 | -694.4826 | -626.8393 | -559.3666 | -492.0654 | -424.9364
HPS New | -347.2504 | -277.1479 | -207.2037 | -137.4186 | -67.7933 | -410.4627 | -341.1596 | -272.0188 | -203.0411 | -134.2272 | -543.3544 | -474.8709 | -406.5537 | -338.4038 | -270.4219 | -756.4826 | -688.8393 | -621.3666 | -554.0654 | -486.9364
LED | -484.3504 | -395.2534 | -306.2197 | -217.2497 | -128.3436 | -39.5017 | 49.2755 | 137.9878 | 226.6349 | 315.2165 | 403.7321 | 492.1815 | 580.5644 | 668.8803 | 757.1291 | 845.3103 | 933.4236 | 1021.4687 | 1109.4452 | 1197.3527

## Slide 45: Sensitivity analysis – Hourly Maintenance Cost
Chart: 20 Year Present Worth Comparison – $161 hourly rate
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 683.8085 | 347.3557 | 1031.1642
 | 1 | 2 | 3

## Slide 46: Sensitivity analysis – Hourly Maintenance Cost
Chart: 20 Year Present Worth Comparison - $350 hourly rate
| 20 Year Present Worth LED vs. HPS | 20 Year Present worth HPS | 20 Year Present Worth LED
 | 1253.2693 | -362.3264 | 890.9429
 | 1 | 2 | 3

## Slide 47: LEDS at Oklahoma Electric Cooperative

## Slide 48: OEC needs
What type of light do we need?
  Not a large amount of street lighting, Almost all security lighting
  100W HPS sodium replacement
What’s important
  Appearance similar to current security lights
  Good protection
  Price

## Slide 49: Protection
Trusted vendor
  Many new players in LED lighting
Limited to vendors that have history of making outdoors enclosures
    Protect against Hail, Tornados, high Winds, Animals, Members
Refractor – Keeps “normal look” while providing additional proctection

## Slide 50: Member response
Urban Members
  Greatly prefer light color
  Enjoy more focus light with less spill
Rural Members
  Dislike that color doesn’t match their existing security lights
  Dislike lack of spill, doesn’t cover the same area(preception)

## Slide 51: Economics - OEC
Energy Cost
  HPS Monthly KW - 40 kw charge - $0.04 yearly cost - $19.20
  LED Monthly KW - 20.4 kw charge - $0.04 yearly cost - $9.79
Maintenance @$150 per truck roll
  HPS – Hours of life 24,000 Lifetime years – 5.06 Yearly cost - $33.61
  LED - Hours of life 75,000 Lifetime years – 15.81 Yearly cost - $12.62
Materials
  Initial Cost – LED is 3 times the cost of HPS
  Replacement cost – LED is 6 times the cost of HPS

## Slide 52: Economic - OEC
Oec charges both security lights at same rate
Years to payoff (break even)
  Kw savings only – 10.8 years
  Maintenance savings only – 6 years
  Total savings – 3.9 years
Equation sensitivity factor
  Anywhere in the range of 3-6 years to payoff