## Slide 1: LED LIGHTING ON BILL BOARDS
Prepared for OPCA by Logan Pleasant, P.E.

## Slide 2: What Does The Load Look Like?
Extreme Load Oscillations
Min-Max load current delta is very high
Sign display can change as often as every 20 seconds
The more white on the sign, the higher the load
Overall demand is fairly low 1-3 kW

## Slide 3: Load Profile Sign 1

## Slide 4: Load Profile Sign 2

## Slide 5: Load Profile Sign 3

## Slide 6: Total Power Sign 1

## Slide 7: Total Power Sign 2

## Slide 8: Total Power Sign 3

## Slide 9: Current Profile Sign 1 I Max = 25A

## Slide 10: Current Profile Sign 2 I Max = 23.5A

## Slide 11: Current Profile Sign 3 I Max = 17

## Slide 12: Harmonic Analysis
Device needs to be IEEE 519 compliant
  THDV <=5%
  TDDC within acceptable levels based on ISC/IL

## Slide 13: Harmonic Analysis

## Slide 14: Total Harmonic Distortion (THD) Sign 1: Need THDV < 5%

## Slide 15: Total Harmonic Distortion (THD) Sign 2: Need THDV < 5%

## Slide 16: Total Harmonic Distortion (THD) Sign 3: Need THDV < 5%

## Slide 17: Harmonic Analysis

## Slide 18: Harmonic Analysis
Sign 1 ISC/IL = 2702/25 = 108
Sign 2 ISC/IL = 2034/23.5 = 87
Sign 3 ISC/IL = 3044/17 = 179
TDD1 < 15%
TDD2 < 12%
TDD3 < 15%

## Slide 19: Total Demand Distortion (TDD) Sign 1: Need TDD < 15%

## Slide 20: Total Demand Distortion (TDD) Sign 2: Need TDD < 12%

## Slide 21: Total Demand Distortion (TDD) Sign 3: Need TDD < 15%

## Slide 22: General Observations
All readings taken at Point of Common Coupling (PCC) – Not at customer load.
Secondary Runs can be very long if necessary, but will exaggerate any harmonic effects at the load
Overall Power Quality is not bad on LED Signs
Could have gotten by with smaller transformers

## Slide 23: General Observations
Signs 2 and 3 met IEEE 519 Standards
Sign 3 was not a dedicated load, so actually would have had even better IEEE 519 stats if taken as a whole system (recommended)
Sign 1 seems to be anomalous
Sign 1 requires further investigation

## Slide 24: Questions?

## Slide 25: Looking Deeper Sign 1

## Slide 26: Looking Deeper Sign 1

## Slide 27: Sign 1 Observations
Very high harmonic content
2nd order harmonics are present
Cycle waveform shows asymmetrical load current
Possibly blown diode on rectifier circuit or design flaw in power supply

## Slide 28: Looking Deeper Sign 1

## Slide 29: Looking Deeper Sign 1

## Slide 30: Looking Deeper Sign 1

## Slide 31: Looking Deeper Sign 1

## Slide 32: Looking Deeper Sign 1

## Slide 33: Looking Deeper Sign 1