## Slide 1: Pole Loading/Make Ready Oklahoma Power and Communications Association 2017 Fall Meeting
Mike Rigney, Ph.D.
Product Manager
Osmose Utilities Services, Inc.

## Slide 2: Course Agenda
Pole Loading Defined
Importance of understanding the ‘code’
  O-Calc Pro demo
Field Data Collection Options
Sensitivity of Pole Loading Parameters
Pole Remaining Strength
NESC Clearance Rules
  O-Calc Pro DMT and Clearance Analysis demo
Resolving Overload Poles (if time permits)
  O-Calc Pro ET Truss Selector demo

## Slide 3: Why Perform Pole Loading?
Any new attachment changes load on a pole
  Increased wind area
  Wire tension
  Offset bending due to equipment weight
Safety requirements as specified by NESC, CSA or GO 95
Reduce risk of legal and financial consequences
Prevent…

## Slide 6: What is Pole Loading Analysis?
A verification that the allowable, remaining strength of the pole is sufficient for the applied load on the pole including any required margins of safety.
Applied Load < Pole Strength

## Slide 7
Pole Strength

## Slide 8
ANSI O5.1-2015 – Wood Poles, Specifications and Dimensions

## Slide 9
Table from Wolfe and Moody (1997):
https://www.fpl.fs.fed.us/documnts/pdf1997/wolfe97b.pdf

## Slide 10
Lc
2 ft
Class 1 4,500 lb
Class 2 3,700 lb
Class 3 3,000 lb
Class 4 2,400 lb
Class 5 1,900 lb
D
Average Bending
Capacity = Lc x D (ft-lb)
Wood Quality
Applied Load
Bending Capacity
Fiber Strength
ANSI O5.1
Notes: Poles of a given class and length are designed to have approximately the same load carrying capacity regardless of species.

## Slide 11
MG/L = .000264 x Fiber Stress x Circumference 3
26”
34”
37,120 ft-lb
83,010 ft-lb
Circumference Increase - 30%
Bending Capacity Increase - 123%
80-90%
Pole’s Bending Strength
In The Outer 2-3” Of Shell!
Circumference3 Effect
Notes: The Groundline bending moment is a function of the fiber stress of the pole times the groundline circumference “cubed”

## Slide 12
Applied Load

## Slide 13
40 mph
Wind
(4 psf)
NESC Winter Storm Load
Heavy Loading District
0.50” Ice
RADIAL ICE ON CONDUCTOR
Span Length * Diameter = Span Area
Span Area * Wind Pressure = Force
Force * Height = Moment
Likewise for equipment on pole
Moments = Total Applied Load

## Slide 14: Design Concept
Problem - Poles become overloaded due new joint use attachments, ice or higher wind loads
New Attachment Location
Pole is Overloaded
Pole Strength
Pole Load
Pole Load with
New Attachment

## Slide 15: National Electrical Safety Code

## Slide 16
HAWAII – WARM ISLANDS
ALASKA - HEAVY
NESC Loading Districts
Heavy
Light
Medium
Notes: NESC Fig 250-1 General Loading Map of United States with respect to Loading of Overhead Lines.

## Slide 17: NESC Loading Districts
 |  | Light | Medium | Heavy
WIND | Cylindrical Surfaces | 9 psf | 4 psf | 4 psf
 | Flat Surfaces | 14.4 psf | 6.4 psf | 6.4 psf
ICE | Temperature | 30o F | 15o F | 0o F
 | Radial Ice | 0 inch | 0.25 inch | 0.5 inch

## Slide 18
Grade | Load Factor | Strength Reduction Factor | Safety Factor | When to Use
B | 2.5 | 0.65 | 2.5/.65 = 3.28 | Highways, Railroads, waterways
C | 1.75 | 0.85 | 1.75/0.85 = 2.06 | 
NESC Construction Grade
Strength Factor
Pole Strength x .65
Pole Strength x .85
<
<
Load Factor
Applied Load x 2.5 (B)
Applied Load x 1.75 (C)

## Slide 19
O-Calc Pro Demo

## Slide 20: Field Data Collection

## Slide 21: Field Data Collection Options
O-Calc LE
IKE 4
Paper

## Slide 22: Field Data Collection - Pole
Pole Owner, Pole Number
Species, Class, Length
Ground Line Circumference
Lat/Long
Digital Images (DMT Image)

## Slide 23: Field Data Collection - Spans
Type
  Wire Diameter, Linear Weight, etc.
Attachment Height
Length
Angles
Tension

## Slide 24: Field Data Collection - Equipment
Type (Dimensions)
  Length, Width, Height (box) or
  Length and Diameter (cylinder)
Weight
Attachment Height
Attachment Angle (side of pole)

## Slide 25: Field Data Collection - Guys
Type (Down, Span, Sidewalk)
Attachment Height(s)
Guy Diameter
Strut Type, Length, and Height
Lead Length and Angle of Anchor
Anchor Type

## Slide 26: Field Collection vs Data Driven PLA
Assume a 100,000 pole plant
Field Data Collection/PLA costs $100/pole
Total cost is $10 million
Data Driven approach ….

## Slide 27: Critical Pole Loading Data
Pole length, class and circumference
Span lengths
Span angles
Wire sizes – power and communication
Wire tensions
Attachment heights for all attachments
Guy size, lead length and orientation
Equipment size and orientation

## Slide 28: Sensitivity of Calculations to Key Input Parameters
Tangent Pole Example – 45/3, NESC Grade B, Light Loading
Wire Diameter
  0.1” Change in Power Wire Diameter = 6% in load
  0.5” Change in Communication Wire Diameter = 6% in load

## Slide 29: Sensitivity of Calculations to Key Input Parameters
Angle Pole Example - 45/3, NESC Grade B, Light Loading, 10 deg angle:
500 lb change in power wire tension = 1000 lb in guy wire
5 deg. change communication wire angle = 400 lb in guy wire
1/8” change in guy wire diameter = 125% change in guy wire capacity

## Slide 30: Pole Remaining Strength

## Slide 31: NESC Reject Criteria
“When a pole loses 1/3
of its original required bending strength
it must be replaced or restored.”

## Slide 32: Decay – Most Critical Location
Load
(Wind Force on Wires, Equip., etc.)
Maximum Stress
(Location Where Pole Breaks)

## Slide 33: NESC Clearance Rules 231-235
http://www.ojua.org/wp-content/uploads/2009/03/Standards-Trifold-revised-8.5x11-5-18-2016.pdf

## Slide 34
Digital Measurement Technology (DMT)
And Clearance Analysis Demo

## Slide 35: Summary
PLA – verification that Pole Strength > Pole Load
Know the Code – which loading district and construction grade
Know the Parameters – Concentrate your fielding or data driven efforts on the more critical parameters
Make Ready – Combination of pole loading and clearance requirements
Don’t Forget – Poles are not static, both their strength and load change over time!

## Slide 36
Probability of Failure – 13.9%
Strength & Load - 1986

## Slide 37
Reduced Strength 25% - 2016
Probability of Failure – 45.9%

## Slide 38
Increased Load 20% - 2017
Probability of Failure – 71.2%

## Slide 39: Resolving Overloaded Poles
Pole Replacement
  High cost
  Coordination between joint owners and attachers
  Long lead time for completion of work
Restoring or Strengthening with Steel Truss Systems
  Typically ¼ the cost of replacement
  Line stays in service
  No coordination delays
  Completed much faster than changeouts

## Slide 40: Are these trusses similar to reinforcing trusses?
Typical Reinforcing Truss
Extended Strengthening Truss
Strengthens Overloaded Portion
Strengthens Groundline

## Slide 41: Design Concept
Solution - The ET-Truss and the pole work together to support the load
Truss Installed to Strengthen Overloaded Portion
Pole Strength
Combined Pole and
Truss Strength
Pole Load

## Slide 42
ET Truss Selector Demo

## Slide 43: Summary
PLA – verification that Pole Strength > Pole Load
Know the Code – which loading district and construction grade
Know the Parameters – Concentrate your fielding or data driven efforts on the more critical parameters
Don’t Forget -- Poles are not static, both their strength and load change over time!

## Slide 44: Questions?
Thank you
  Mike Rigney
  315.385.3842
mrigney@osmose.com
www.osmose.com

## Slide 45: California Public Utility Commission General Order 95
http://www.cpuc.ca.gov/gos/GO95/go_95_startup_page.html

## Slide 46: GO 95 Loading Districts

## Slide 47: GO95 Loading Districts
 |  | Light | Heavy*
WIND | Cylindrical Surfaces | 8 psf | 6 psf
 | Flat Surfaces | 13 psf | 10 psf
ICE | Temperature | 25o F | 0o F
 | Radial Ice | 0 inch | 0.5 inch
* GO 95 Heavy loading district is comparable to NESC Medium loading district.

## Slide 48: GO95 Grades of Construction
Grade | Strength Reduction Factor | Safety Factor | When to Use
A | 0.25 | 4 | Primary Voltages and Communication
B | 0.33 | 3 | Primary Voltages
C | 0.5 | 2 | Communication
Safety Factor
Applied Load x 4 (A)
Applied Load x 3 (B)
Applied Load x 2 (C)
<
<
Pole Strength
Pole Strength
Pole Strength
<

## Slide 49: Canadian Standards Association C23.3 No. 1-15, Overhead systems

## Slide 50: CSA 2015 Loading Districts

## Slide 51: CSA 2015 Loading Districts
 | Medium A | Medium B | Heavy | Severe
Wind | 400 N/m2 | 300 N/m2 | 400 N/m2 | 400 N/m2
Ice | 6.5 mm | 12.5 mm | 12.5 mm | 19 mm
Temperature | -20 oC | -20 oC | -20 oC | -20 oC

## Slide 52: CSA 2015 Grades of Construction
Grade | Vertical Load Factor | Transverse Load Factor | When to Use
1 | 2.00 | 1.90 | railways, controlled-access highways, navigable waters
2 | 1.50 | 1.30 | Supply lines of any voltage
3 | 1.20 | 1.10 | General, other private or public property
Safety Factor
Applied Load x 1.9 (1)
Applied Load x 1.3 (2)
Applied Load x 1.1 (3)
<
<
Pole Strength
Pole Strength
Pole Strength
<