## Slide 1: SOLAR PHOTOVOLTAIC POWER SYSTEMS
INTERNATIONAL FIRE CODE 2015

## Slide 2: INTERNATIONAL FIRE CODE 2015 CHAPTER 6
The greatest danger facing emergency responders operating in proximity to solar energy collection systems is the lack of knowledge needed to operate safely around these systems. Some of the potential hazards associated with PV systems are tripping hazards and/or falls for the fire fighters operating on the roof and the potential for earlier roof collapse due to the added dead load and electric shock.

## Slide 3: INTERNATIONAL FIRE CODE 2015 CHAPTER 6
605.11.1 – Access and Pathways. Roof access, pathways, and spacing requirements shall be provided in accordance with Sections 605.11.1.1 through 605.11.1.3.3
  Exceptions:
    1. Detached non-habitable Group-U structures……carports, solar trellises and similar structures
    2. Roof Access, pathways and spacing requirements need not be provided where the fire chief has determined that rooftop operations will not be employed

## Slide 4: INTERNATIONAL FIRE CODE 2015 CHAPTER 6
605.11.1.1 - Roof Access Points. Roof access points shall be located in areas that do not require the placement of ground ladders over openings such as windows or doors, and located at strong points of building construction in locations where the access point does not conflict with overhead obstructions such as tree limbs, wires or signs.