## Slide 1
Is A Pole Safe To Climb?
Notes: Safety is one of the biggest expectations for every OUS employee. It is a condition of employment.
Having a successful Safety Program, building a strong Safety Culture and seeing the benefits of those in the form of excellent safety statistics doesn’t happen by accident…..it takes active management. And it is something that we are very proud of at Osmose.

## Slide 2
Pole Design

## Slide 3: Design for Bending Loads
Bending Load
Bending Capacity
>
Wire with Ice
Notes: When designing a line, you must select the right pole size for both clearance and strength. Jason has spoken to you about clearances, now we can look at strength. A poles bending capacity must be greater than the bending loads being applied to a pole. There are codes and standard that will help with determining the strength of a pole and the appropriate loads to apply to the pole…..

## Slide 4: Design for Bending Loads
Bending Load
Bending Capacity
>
Wire with Ice
Notes: When designing a line, you must select the right pole size for both clearance and strength. Jason has spoken to you about clearances, now we can look at strength. A poles bending capacity must be greater than the bending loads being applied to a pole. There are codes and standard that will help with determining the strength of a pole and the appropriate loads to apply to the pole…..

## Slide 5: Design for Bending Loads
Bending Capacity
Selecting a Pole with appropriate capacity
Class is determined by the load on the pole
Length is determined by required clearance
Notes: When designing a line, you must select the right pole size for both clearance and strength. Jason has spoken to you about clearances, now we can look at strength. A poles bending capacity must be greater than the bending loads being applied to a pole. There are codes and standard that will help with determining the strength of a pole and the appropriate loads to apply to the pole…..

## Slide 6: Design for Bending Loads
Bending Load
Wire with Ice
Load types acting on the pole:
    Wind
    Ice
    Line Tension
    Guy Tension
    Weight (equipment, conductors, etc)
Notes: When designing a line, you must select the right pole size for both clearance and strength. Jason has spoken to you about clearances, now we can look at strength. A poles bending capacity must be greater than the bending loads being applied to a pole. There are codes and standard that will help with determining the strength of a pole and the appropriate loads to apply to the pole…..

## Slide 7
HAWAII - LIGHT
ALASKA - HEAVY
NESC Loading Districts
Heavy
Light
Medium
Notes: NESC Fig 250-1 General Loading Map of United States with respect to Loading of Overhead Lines.

## Slide 8
40 mph
Wind
NESC Winter Storm Load
Heavy Loading District
.50” Ice
RADIAL ICE ON CONDUCTOR

## Slide 10
        Crossing Limited Access Hwy B 4
        Crossing Railroads B 4
        Crossing Some Wires B 4
        Otherwise ` C 2
NESC Grade of Construction

## Slide 11
900 lb
Storm Load
x 4 (Grade B)
Class 1 4500 lb
Class 2 3700 lb
Class 3 3000 lb
Class 4 2400 lb
Class 5 1900 lb
= 3600 lb
NESC
ANSI O5.1
Load < Strength

## Slide 12
900 lb
Storm Load
x 2 (Grade C)
Class 1 4500 lb
Class 2 3700 lb
Class 3 3000 lb
Class 4 2400 lb
Class 5 1900 lb
= 1800 lb
NESC
ANSI O5.1
Load < Strength

## Slide 13: NESC Overload & Safety Factors
2/3
2/3

## Slide 14: NESC Reject Criteria
“When a pole loses 1/3 or 33% of its original required bending strength
or
13% of it’s original circumference, it must be replaced or restored.”

## Slide 15
How Does A Pole Go Bad….

## Slide 16: Wood Poles Decay
Eventually, all poles deteriorate over time
  Preservative migration and
  degradation in sapwood
  Surface checking exposes
  unpreserved heartwood
  Weathering (surface erosion)
  Mechanical damage
  Animal damage
Notes: Regardless of treatment quality – penetration and retention……Even with sufficient chemical protection, all wood poles will eventually succumb to the action of decay and insects.
We have answered the “Why” now lets take a look at the “How” part of wood pole decay.
Wood will decay over time because the original preservative will breakdown declining to a point where the chemicals are below the fungitoxic threshold and won’t continue to protect the wood.
Below ground decay is the number one reason why poles fail NESC related strength inspections. Decay is followed by Mechanical Damage, Animal Damage, and Pole Top Decay.

## Slide 17: Wood Poles Decay
Deep Checking- penetrates beyond treatment zone (sapwood zone)
Allow entry point for moisture, fungal spores and insects

## Slide 18
Decayed but Serviceable
Below Code Required Strength
67% or less
Greater than 67% remaining strength
No Decay
Wood Pole Aging Process

## Slide 19: Wood Poles Decay
Notes: In most cases, the first occurrence of decay will be just below the groundline. This is where the conditions of moisture, temperature, oxygen (air) and the absence of direct sunlight are most favorable to the growth of fungi.
Unfortunately, this is a portion of the pole usually hidden from view and it is close to the natural breaking point of a pole under strain. Thus, it is the most critical part of the pole and warrants special inspection and maintenance.
Below ground decay is the number one reason why poles fail NESC related strength inspections. Decay is followed by Mechanical Damage, Animal Damage, and Pole Top Decay.

## Slide 20: Wood Poles Decay
AWPA Deterioration Zones
Zone 5 – SEVERE
Zone 4 – HIGH
Zone 3 – INTERMEDIATE
Zone 2 – MODERATE
Zone 1 – LOW
Notes: Rate of decay is also dependent and the geographical location of the pole. AWPA has established decay zones based on rain fall, average temperature

## Slide 21: Internal Decay
Generally associated with thin sapwood species (firs, cedars)
Characterized by soft ”punky” heartwood and/or open voids
Most often associated with brown rot decay
Advanced Internal Decay
Early Internal Decay
Notes: Internal deterioration of a treated pole is due very largely to development of checks after treatment that expose the untreated heartwood to decay and insects.

## Slide 22: External Decay
Generally associated with thick sapwood species (pines)
Characterized by loose/fibrous shell
Most often associated with soft rot decay
Notes: External decay is a consequence of gradual loss of preservative in the sapwood through degradation, evaporation, and chemical change.

## Slide 23: External Decay
18”
Pole Butt
G/L
Southern Pine Poles tend to decay below ground from the outside in.
90% of the poles strength in the outer 2 – 3 inches of shell.

## Slide 24: Reject Pole Examples

## Slide 25: Reject Pole Examples

## Slide 26: Reject Pole Examples

## Slide 27: Reject Pole Examples

## Slide 28: Decay @ Most Critical Location
Load
(Wind Force on Wires, Equip., etc.)
Maximum Stress
(Location Where Likely to Break)

## Slide 29: 13% Loss of Required Circumference = NESC Reject 33% of Required Strength Loss = NESC Reject
Evaluating Pole Strength

## Slide 30
Inspection Programs

## Slide 31
Pole Inspection Techniques

## Slide 32: Inspection Methods
Visual Only
Advantages
Lowest cost per pole. Go through system faster with less money.
Culls out the obvious above ground rejects quicker with less money being spent.
Disadvantages
Least accurate inspection. Leaves a considerable number of undetected rejects in the system, along with liability and reliability risks. Will miss priority poles with groundline decay.
Annual inspection cycles are recommended.
Rejects ratios remain high in future cycles.
100% cost, no return as earnings.

## Slide 33: Inspection Methods
Visual & Sound
Advantages
Lower cost per pole. Go through system faster with less money.
Culls out the obvious above ground rejects quicker with less money being spent.
Disadvantages
Less accurate inspection. Leaves a considerable number of undetected rejects in the system, along with liability and reliability risks. May miss priority poles with groundline decay. Locates 15-25% of rejects.
Nothing is done to extend service life, so 2-4 year inspection cycles are recommended.
Rejects ratios remain high in future cycles.
100% cost, no return as earnings.

## Slide 34: Inspection Methods
Sound & Bore Inspection

## Slide 35: Inspection Methods
Sound & Bore/Partial Excavate/Selective Treat
70-

## Slide 36: Inspection Methods
Full Excavate & Groundline Treat
98 % of rejects.

## Slide 37
From
The Effectiveness of Pole Maintenance Programs Varies Greatly
Finding a Small Portion of the Poles
Below Code Strength
To
Finding 98% of all Decayed Poles and Extending Pole Service Life

## Slide 38
So What Should I do Before I Climb???

## Slide 39: Pre-Climb Inspection
Follow Company approved pre-climb inspection procedures

## Slide 40: Pre-Climb Inspection
Follow Company approved pre-climb inspection procedures
  Visually Inspect the pole from top to bottom
      Decayed Tops
      Split Tops
      Wood Pecker Damage
      Animal Damage
      Loose Equipment
      Mechanical Damage
      Previous Inspection Tags

## Slide 41: Reject Tags

## Slide 42: Inspection Tags

## Slide 43: Pre-Climb Inspection
Follow Company approved pre-climb inspection procedures
  Visually Inspect the pole from top to bottom
  Sound pole
      Sound all sides and from groundline
      to as high as you can reach.

## Slide 44: Pre-Climb Inspection
Follow Company approved pre-climb inspection procedures
  Visually Inspect the pole from top to bottom
  Sound pole. Sound all sides and from groundline to as high as you can reach
  Evaluate Groundline. Look for mold mold, decaying wood, and below ground rot.

## Slide 45: Pre-Climb Inspection
Follow Company approved pre-climb inspection procedures
  Visually Inspect the pole from top to bottom
  Sound pole.
  Evaluate Groundline
  Look below Groundline
      One or Two sided Pull Back
One Sided
Two Sided

## Slide 46: Pre-Climb Inspection
Follow Company approved pre-climb inspection procedures
  Visually Inspect the pole from top to bottom
  Inspection condition of banding and truss
  Sound pole. Concentrate around lower banding area and near of the truss
  Bore inspection holes in lower banding area and top of truss for min shell requirements
  If inspection finds any one area falls below minimum requirements, the pole should not be climbed and reported to appropriate utility leadership for further evaluation or replacement

## Slide 47: Climbing A Trussed Pole

## Slide 48
Questions?

## Slide 49
Osmose University
Wood Pole Plant Management Seminar
Steel Structure Plant Management Seminar

## Slide 51
Rex Harris
940-782-9072
rharris@osmose.com www.osmoseutilities.com