## Slide 1: Why Consumers Need to Provide Their Own Surge Protection
Jon Joyce P.E., Consulting Electrical Engineer, Edmond, OK

## Slide 2: Isn’t the power company supposed to provide “clean” power?

## Slide 3: News Flash…… “… the engineering reality of a large power system is that disturbances are unavoidable.”

## Slide 4: Utilities have standards for voltage ranges, frequency, distortion, and interruptions…

## Slide 5: …but there are several types of voltage disturbances that the power company cannot control.

## Slide 6: Any of these disturbances can cause system failures or damage electronic and digital equipment.
How often do you experience unexplained equipment failure or misoperation?

## Slide 7: Transient Voltage Surge Disturbance

## Slide 8: A 2 year IBM study at 200 locations in 25 cities showed 85% of power problems are transient voltage related.

## Slide 9: A transient surge is a very short duration (sub-cycle)voltage disturbance and can range from 1X to more than 50X normal voltage in building wiring systems.

## Slide 10
Insulation breakdown or arcing.
Surge protective device failure.
Semiconductor device failure.
Power conversion equipment nuisance trip.
Data processing equipment malfunction.
Transient surge effects depend on surge energy

## Slide 11: Lightning is often a source of high energy voltage surge

## Slide 12: Lightning (high energy) damage is often easy to recognize….

## Slide 13: But…… Lower energy surges usually originate inside the building. Low energy surge damage may not be visible to the eye.

## Slide 14: Low energy surges can lock-up operating systems or damage digital gear. Dranetz Handbook for Power Quality

## Slide 15: Studies have shown that 60% to 80% of surges originate inside the building. Some inside surge sources: HVAC Pumps VSD Equipment Printers & Copiers HE Lighting

## Slide 16: Who is responsible for disturbance protection?

## Slide 17: The consumer is responsible for making sure the facility power system is compatible with the end-use equipment.
The power company will deliver a basic level of power quality.
The consumer should design their facility to provide the necessary level of PQ for their equipment.

## Slide 18: The basic design guide for power quality compatibility is IEEE Standard 1100.
The Emerald Book is a consensus standard for commercial and industrial consumers operating electronic equipment.

## Slide 19: Cascaded SPDs are required to protect the load from a transient surge events.
SPDs built into the end-use equipment aren’t rated to stop a large surge.
SPDs used at the service entrance can still let through a significant surge.
Surges originating inside the building require intermediate SPD locations.

## Slide 20: How does an SPD work?
When a voltage spike occurs the SPD responds in nanoseconds by creating a short circuit through itself (almost like closing a switch).
The low impedance path through the SPD shunts most (but not all) of the surge away from the load.

## Slide 21: SPDs come in many shapes and sizes
SPDs are classified depending on the intended application and voltage/current ratings.
Most electronic equipment now contains internal SPDs that only protect against low energy surges.

## Slide 22: The heart of most surge protection devices is the Metal Oxide Varistor
Virtually all modern surge protectors, regardless of size or rating, use metal-oxide varistor (MOV) technology.
These are the individual MOV components that can be packaged in different ways depending on the rating and application.
Other types of surge suppressors are Silicon Carbide, Gas Tube, and Spark Gap

## Slide 23: Note that SPDs ONLY protect against transient surges.
Will not protect against short duration sags and swells.
Will not protect against blinks or power outages.
Will not protect against EMI/RFI noise (unless it also includes filter circuitry).

## Slide 24: SPD Application

## Slide 25: The electric utility installs surge arresters on most of its transformers.

## Slide 26: The utility’s arrester protects utility equipment, not yours.
Utility equipment is designed to withstand very high surge voltages of 95 kV and above.
The utility arrester has to pass very high surge currents to survive in this environment.
A significant surge can still reach your building.

## Slide 27: Multiple SPDs arranged in a cascaded system are required for effective protection.
Schneider Electric
Critical
Load

## Slide 28: Service Entrance…. the consumer installs a properly sized SPD at the service entrance.
Critical
Load

## Slide 29: Intermediate Panels… SPDs are installed at subpanels feeding critical equipment.
Surge originating inside the building
Critical
Load

## Slide 30: End Use Equipment… Microprocessor based equipment should have internal SPDs.
Surge originating inside the building
Critical
Load

## Slide 31: Working together, the cascaded system will provide the best possible surge protection.
Surge originating inside the building
Critical
Load

## Slide 32: The NEC now requires the use of SPDs in certain situations…..
The NEC 2011 Edition first recognized that sensitive electronic controls used in safety systems require SPDs.
The 2017 NEC now requires listed SPDs for:
  Emergency Power Systems Switchgear
  Elevators, Escalators, Moving Walks, Lifts, and Stairway Chair Lifts
  Critical Operations Data Systems
  Industrial Machinery using Safety Interlocks
The NEC requires all SPDs to meet listing and installation requirements.

## Slide 33: All SPDs used in consumer installations must be UL listed devices
UL Type 1
Line or load side of service entrance locations. Can be installed without external overcurrent device. Discharge current rated 10 or 20 kA.
UL Type 2
Load side of service entrance, An overcurrent disconnect is required. Discharge current ratings of 3, 5, 10, or 20 kA.
UL Type 3
Plug-in or cord-connected SPDs used at point of utilization.

## Slide 34: IEEE SPD Location Categories
Location category depict the surge environment.
Surge currents decrease as you get further into the building wiring system.

## Slide 35: The SPD UL type should be used in the appropriate IEEE category location.
UL Type 1
UL Type 2
UL Type 3
Surge energy decreases with distance from the service entrance

## Slide 36: An Example Installation

## Slide 37: Utility Office Building The critical load is the equipment powering the enterprise servers.
1200A
Main Distribution
Panel
400A
Emergency
Distribution
Panel
200A
UPS
Disc.
Switch
Server
Room
UPS
150 kW
Genset
400A
Automatic
Transfer
Switch
To Utility Source
Enterprise Servers

## Slide 38: Add UL Type 1 SPD at Main Panel
1200A
Main Distribution
Panel
400A
Emergency
Distribution
Panel
200A
UPS
Disc.
Switch
Server
Room
UPS
150 kW
Genset
400A
Automatic
Transfer
Switch
To Utility Source

## Slide 39: Add UL Type 1 SPD at Emergency Panel (The emergency system is also fed from outside the building)
1200A
Main Distribution
Panel
400A
Emergency
Distribution
Panel
200A
UPS
Disc.
Switch
Server
Room
UPS
Outdoor
150 kW
Genset
400A
Automatic
Transfer
Switch
To Utility Source

## Slide 40: Add UL Type 2 SPD at UPS Panel
1200A
Main Distribution
Panel
400A
Emergency
Distribution
Panel
200A
UPS
Disc.
Switch
Server
Room
UPS
150 kW
Genset
400A
Automatic
Transfer
Switch
To Utility Source

## Slide 41: SPD Equipment as Installed
1200A
Main Distribution
Panel
400A
Emergency
Distribution
Panel
200A
UPS
Disc.
Switch
Server
Room
UPS
150 kW
Genset
400A
Automatic
Transfer
Switch
To Utility Source

## Slide 42: Effective surge protection depends on…
Cascading SPDs for optimum protection of critical equipment.
Specifying the appropriate SPD for each location to insure reliable operation and long life.
Proper installation of each SPD to insure maximum effectiveness.

## Slide 43: Thank You!
Any questions?